## Slide 1: Induction Motors

## Slide 2: Introduction
Three-phase induction motors are the most common and frequently encountered machines in industry
  simple design, rugged, low-price, easy maintenance
  wide range of power ratings: fractional horsepower to 10 MW
  run essentially as constant speed from no-load to full load
  Its speed depends on the frequency of the power source
    not easy to have variable speed control
    requires a variable-frequency power-electronic drive for optimal speed control

## Slide 3: Construction
An induction motor has two main parts
  a stationary stator
    consisting of a steel frame that supports a hollow, cylindrical core
    core, constructed from stacked laminations (why?), having a number of evenly spaced slots, providing the space for the stator winding
Stator of IM

## Slide 4: Construction
  a revolving rotor
    composed of punched laminations, stacked to create a series of rotor slots, providing space for the rotor winding
    one of two types of rotor windings
    conventional 3-phase windings made of insulated wire (wound-rotor) » similar to the winding on the stator
    aluminum bus bars shorted together at the ends by two aluminum rings, forming a squirrel-cage shaped circuit (squirrel-cage)
Two basic design types depending on the rotor design
  squirrel-cage: conducting bars laid into slots and shorted at both ends by shorting rings.
  wound-rotor: complete set of three-phase windings exactly as the stator. Usually Y-connected, the ends of the three rotor wires are connected to 3 slip rings on the rotor shaft. In this way, the rotor circuit is accessible.

## Slide 5: Construction
Squirrel cage rotor
Wound rotor
Notice the slip rings

## Slide 6: Construction
Cutaway in a typical wound-rotor IM. Notice the brushes and the slip rings
Brushes
Slip rings

## Slide 7: Rotating Magnetic Field
Balanced three phase windings, i.e. mechanically displaced 120 degrees form each other, fed by balanced three phase source
A rotating magnetic field with constant magnitude is produced, rotating with a speed
Where fe is the supply frequency and
P is the no. of poles and nsync is called the synchronous speed in rpm (revolutions per minute)

## Slide 8: Synchronous speed
P | 50 Hz | 60 Hz
2 | 3000 | 3600
4 | 1500 | 1800
6 | 1000 | 1200
8 | 750 | 900
10 | 600 | 720
12 | 500 | 600

## Slide 9: Rotating Magnetic Field

## Slide 10: Rotating Magnetic Field

## Slide 11: Rotating Magnetic Field

## Slide 12: Rotating Magnetic Field

## Slide 13: Rotating Magnetic Field

## Slide 14: Principle of operation
This rotating magnetic field cuts the rotor windings and produces an induced voltage in the rotor windings
Due to the fact that the rotor windings are short circuited, for both squirrel cage and wound-rotor, and induced current flows in the rotor windings
The rotor current produces another magnetic field
A torque is produced as a result of the interaction of those two magnetic fields
Where ind is the induced torque and BR and BS are the magnetic flux densities of the rotor and the stator respectively

## Slide 15: Induction motor speed
At what speed will the IM run?
  Can the IM run at the synchronous speed, why?
  If rotor runs at the synchronous speed, which is the same speed of the rotating magnetic field, then the rotor will appear stationary to the rotating magnetic field and the rotating magnetic field will not cut the rotor. So, no induced current will flow in the rotor and no rotor magnetic flux will be produced so no torque is generated and the rotor speed will fall below the synchronous speed
  When the speed falls, the rotating magnetic field will cut the rotor windings and a torque is produced

## Slide 16: Induction motor speed
So, the IM will always run at a speed lower than the synchronous speed
The difference between the motor speed and the synchronous speed is called the Slip
  Where nslip= slip speed
  nsync= speed of the magnetic field
  nm = mechanical shaft speed of the motor

## Slide 17: The Slip
Where s is the slip
Notice that : if the rotor runs at synchronous speed
s = 0
if the rotor is stationary
s = 1
Slip may be expressed as a percentage by multiplying the above eq. by 100, notice that the slip is a ratio and doesn’t have units

## Slide 18: Induction Motors and Transformers
Both IM and transformer works on the principle of induced voltage
  Transformer: voltage applied to the primary windings produce an induced voltage in the secondary windings
  Induction motor: voltage applied to the stator windings produce an induced voltage in the rotor windings
  The difference is that, in the case of the induction motor, the secondary windings can move
  Due to the rotation of the rotor (the secondary winding of the IM), the induced voltage in it does not have the same frequency of the stator (the primary) voltage

## Slide 19: Frequency
The frequency of the voltage induced in the rotor is given by
  Where fr = the rotor frequency (Hz)
  P = number of stator poles
  n = slip speed (rpm)

## Slide 20: Frequency
What would be the frequency of the rotor’s induced voltage at any speed nm?
When the rotor is blocked (s=1) , the frequency of the induced voltage is equal to the supply frequency
On the other hand, if the rotor runs at synchronous speed (s = 0), the frequency will be zero

## Slide 21: Torque
While the input to the induction motor is electrical power, its output is mechanical power and for that we should know some terms and quantities related to mechanical power
Any mechanical load applied to the motor shaft will introduce a Torque on the motor shaft. This torque is related to the motor output power and the rotor speed
and

## Slide 22: Horse power
Another unit used to measure mechanical power is the horse power
It is used to refer to the mechanical output power of the motor
Since we, as an electrical engineers, deal with watts as a unit to measure electrical power, there is a relation between horse power and watts

## Slide 23: Example
A 208-V, 10hp, four pole, 60 Hz, Y-connected induction motor has a full-load slip of 5 percent
  What is the synchronous speed of this motor?
  What is the rotor speed of this motor at rated load?
  What is the rotor frequency of this motor at rated load?
  What is the shaft torque of this motor at rated load?

## Slide 24: Solution

## Slide 25: Equivalent Circuit
The induction motor is similar to the transformer with the exception that its secondary windings are free to rotate
  As we noticed in the transformer, it is easier if we can combine these two circuits in one circuit but there are some difficulties

## Slide 26: Equivalent Circuit
When the rotor is locked (or blocked), i.e. s =1, the largest voltage and rotor frequency are induced in the rotor, Why?
On the other side, if the rotor rotates at synchronous speed, i.e. s = 0, the induced voltage and frequency in the rotor will be equal to zero, Why?
  Where ER0 is the largest value of the rotor’s induced voltage obtained at s = 1(loacked rotor)

## Slide 27: Equivalent Circuit
The same is true for the frequency, i.e.
It is known that
So, as the frequency of the induced voltage in the rotor changes, the reactance of the rotor circuit also changes
Where Xr0 is the rotor reactance
at the supply frequency
(at blocked rotor)

## Slide 28: Equivalent Circuit
Then, we can draw the rotor equivalent circuit as follows
  Where ER is the induced voltage in the rotor and RR is the rotor resistance

## Slide 29: Equivalent Circuit
Now we can calculate the rotor current as
Dividing both the numerator and denominator by s so nothing changes we get
  Where ER0 is the induced voltage and XR0 is the rotor reactance at blocked rotor condition (s = 1)

## Slide 30: Equivalent Circuit
Now we can have the rotor equivalent circuit

## Slide 31: Equivalent Circuit
Now as we managed to solve the induced voltage and different frequency problems, we can combine the stator and rotor circuits in one equivalent circuit
  Where

## Slide 32: Power losses in Induction machines
Copper losses
  Copper loss in the stator (PSCL) = I12R1
  Copper loss in the rotor (PRCL) = I22R2
Core loss (Pcore)
Mechanical power loss due to friction and windage
How this power flow in the motor?

## Slide 33: Power flow in induction motor

## Slide 34: Power relations

## Slide 35: Equivalent Circuit
We can rearrange the equivalent circuit as follows
Actual rotor resistance
Resistance equivalent to mechanical load

## Slide 36: Power relations

## Slide 37: Power relations
1
s
1-s

## Slide 38: Example
A 480-V, 60 Hz, 50-hp, three phase induction motor is drawing 60A at 0.85 PF lagging. The stator copper losses are 2 kW, and the rotor copper losses are 700 W. The friction and windage losses are 600 W, the core losses are 1800 W, and the stray losses are negligible. Find the following quantities:
  The air-gap power PAG.
  The power converted Pconv.
  The output power Pout.
  The efficiency of the motor.

## Slide 39: Solution

## Slide 40: Solution

## Slide 41: Example
A 460-V, 25-hp, 60 Hz, four-pole, Y-connected induction motor has the following impedances in ohms per phase referred to the stator circuit:
R1= 0.641 R2= 0.332
X1= 1.106  X2= 0.464  XM= 26.3 
The total rotational losses are 1100 W and are assumed to be constant. The core loss is lumped in with the rotational losses. For a rotor slip of 2.2 percent at the rated voltage and rated frequency, find the motor’s
  Speed
  Stator current
  Power factor
Pconv and Pout
ind and load
Efficiency

## Slide 42: Solution

## Slide 43: Solution

## Slide 44: Solution

## Slide 45: Torque, power and Thevenin’s Theorem
Thevenin’s theorem can be used to transform the network to the left of points ‘a’ and ‘b’ into an equivalent voltage source VTH in series with equivalent impedance RTH+jXTH

## Slide 46: Torque, power and Thevenin’s Theorem

## Slide 47: Torque, power and Thevenin’s Theorem
Since XM>>X1 and XM>>R1
Because XM>>X1 and XM+X1>>R1

## Slide 48: Torque, power and Thevenin’s Theorem
Then the power converted to mechanical (Pconv)
And the internal mechanical torque (Tconv)

## Slide 49: Torque, power and Thevenin’s Theorem

## Slide 50: Torque-speed characteristics
Typical torque-speed characteristics of induction motor

## Slide 51: Comments
The induced torque is zero at synchronous speed. Discussed earlier.
The curve is nearly linear between no-load and full load. In this range, the rotor resistance is much greater than the reactance, so the rotor current, torque increase linearly with the slip.
There is a maximum possible torque that can’t be exceeded. This torque is called pullout torque and is 2 to 3 times the rated full-load torque.

## Slide 52: Comments
The starting torque of the motor is slightly higher than its full-load torque, so the motor will start carrying any load it can supply at full load.
The torque of the motor for a given slip varies as the square of the applied voltage.
If the rotor is driven faster than synchronous speed it will run as a generator, converting mechanical power to electric power.

## Slide 53: Complete Speed-torque c/c

## Slide 54: Maximum torque
Maximum torque occurs when the power transferred to R2/s is maximum.
This condition occurs when R2/s equals the magnitude of the impedance RTH + j (XTH + X2)

## Slide 55: Maximum torque
The corresponding maximum torque of an induction motor equals
The slip at maximum torque is directly proportional to the rotor resistance R2
The maximum torque is independent of R2

## Slide 56: Maximum torque
Rotor resistance can be increased by inserting external resistance in the rotor of a wound-rotor induction motor.
The
value of the maximum torque remains unaffected
but
the speed at which it occurs can be controlled.

## Slide 57: Maximum torque
Effect of rotor resistance on torque-speed characteristic

## Slide 58: Example
  A two-pole, 50-Hz induction motor supplies 15kW to a load at a speed of 2950 rpm.
  What is the motor’s slip?
  What is the induced torque in the motor in N.m under these conditions?
  What will be the operating speed of the motor if its torque is doubled?
  How much power will be supplied by the motor when the torque is doubled?

## Slide 59: Solution

## Slide 60: Solution
  In the low-slip region, the torque-speed curve is linear and the induced torque is direct proportional to slip. So, if the torque is doubled the new slip will be 3.33% and the motor speed will be

## Slide 61: Example
  A 460-V, 25-hp, 60-Hz, four-pole, Y-connected wound-rotor induction motor has the following impedances in ohms per phase referred to the stator circuit
R1= 0.641 R2= 0.332
X1= 1.106  X2= 0.464  XM= 26.3 
  What is the maximum torque of this motor? At what speed and slip does it occur?
  What is the starting torque of this motor?
  If the rotor resistance is doubled, what is the speed at which the maximum torque now occur? What is the new starting torque of the motor?
  Calculate and plot the T-s c/c for both cases.

## Slide 62: Solution

## Slide 63: Solution
  The corresponding speed is

## Slide 64: Solution
  The torque at this speed is

## Slide 65: Solution
  The starting torque can be found from the torque eqn. by substituting s = 1

## Slide 66: Solution
  If the rotor resistance is doubled, then the slip at maximum torque doubles too
  The corresponding speed is
  The maximum torque is still
  max = 229 N.m

## Slide 67: Solution
  The starting torque is now

## Slide 68: Determination of motor parameters
Due to the similarity between the induction motor equivalent circuit and the transformer equivalent circuit, same tests are used to determine the values of the motor parameters.
  DC test: determine the stator resistance R1
  No-load test: determine the rotational losses and magnetization current (similar to no-load test in Transformers).
  Locked-rotor test: determine the rotor and stator impedances (similar to short-circuit test in Transformers).

## Slide 69: DC test
  The purpose of the DC test is to determine R1. A variable DC voltage source is connected between two stator terminals.
  The DC source is adjusted to provide approximately rated stator current, and the resistance between the two stator leads is determined from the voltmeter and ammeter readings.

## Slide 70: DC test
  then
  If the stator is Y-connected, the per phase stator resistance is
  If the stator is delta-connected, the per phase stator resistance is

## Slide 71: No-load test
  The motor is allowed to spin freely
  The only load on the motor is the friction and windage losses, so all Pconv is consumed by mechanical losses
  The slip is very small

## Slide 72: No-load test
  At this small slip
  The equivalent circuit reduces to…

## Slide 73: No-load test
  Combining Rc & RF+W we get……

## Slide 74: No-load test
  At the no-load conditions, the input power measured by meters must equal the losses in the motor.
  The PRCL is negligible because I2 is extremely small because R2(1-s)/s is very large.
  The input power equals
  Where

## Slide 75: No-load test
  The equivalent input impedance is thus approximately
  If X1 can be found, in some other fashion, the magnetizing impedance XM will be known

## Slide 76: Blocked-rotor test
In this test, the rotor is locked or blocked so that it cannot move, a voltage is applied to the motor, and the resulting voltage, current and power are measured.

## Slide 77: Blocked-rotor test
The AC voltage applied to the stator is adjusted so that the current flow is approximately full-load value.
The locked-rotor power factor can be found as
The magnitude of the total impedance

## Slide 78: Blocked-rotor test
  Where X’1 and X’2 are the stator and rotor reactances at the test frequency respectively

## Slide 79: Blocked-rotor test
 | X1 and X2 as function of XLR | 
Rotor Design | X1 | X2
Wound rotor | 0.5 XLR | 0.5 XLR
Design A | 0.5 XLR | 0.5 XLR
Design B | 0.4 XLR | 0.6 XLR
Design C | 0.3 XLR | 0.7 XLR
Design D | 0.5 XLR | 0.5 XLR

## Slide 80: Example
  The following test data were taken on a 7.5-hp, four-pole, 208-V, 60-Hz, design A, Y-connected IM having a rated current of 28 A.
  DC Test:
  VDC = 13.6 V IDC = 28.0 A
  No-load Test:
  Vl = 208 V f = 60 Hz
  I = 8.17 A Pin = 420 W
  Locked-rotor Test:
  Vl = 25 V f = 15 Hz
  I = 27.9 A Pin = 920 W
  Sketch the per-phase equivalent circuit of this motor.
  Find the slip at pull-out torque, and find the value of the pull-out torque.