## Slide 1: Negative Sequence Compensation via GSC and RSC to mitigate Stator Voltage Unbalance in DFIG
M. Shamaas
2018-MS-EE-4

## Slide 2: Stator Voltage Unbalance and Negative Sequence Components
Negative-sequence components rotate at - in dq- reference frame.
They are extracted through abc/qd− transformation and LPFs.

## Slide 3: Stator Phase a Voltage Collapses to zero for t=10s to t=15s

## Slide 4: Complete DFIG Simulation Model

## Slide 5: Induction Machine dq0-axis Model
Voltage and Current Equations
Motion and Torque Equations

## Slide 6: Induction Machine Model

## Slide 7: DFIG Rotor Side Converter Positive Sequence Control
The output real and reactive power from the stator circuit can be controlled via iqr and idr respectively.

## Slide 8: Positive Sequence Controller in RSC

## Slide 9: Positive Sequence RSC Control of Stator Power Qs

## Slide 10: Positive Sequence RSC Control of Stator Power Ps

## Slide 11: DFIG Rotor Side Converter Negative Sequence Control
For a given negative-sequence stator voltage, a negative sequence rotor voltage generated by the RSC has the potential to eliminate the negative sequence rotor current, the negative sequence stator current or the torque pulsation.
RSC must make and by controlling and .

## Slide 12: Negative Sequence Controller in RSC

## Slide 13: Negative Sequence Compensation via RSC

## Slide 14: Torque Response

## Slide 15: DFIG Grid Side Converter Positive Sequence Control
The GSC is used for real power and reactive power control
GSC control should take care of the DC-link voltage

## Slide 16: Positive Sequence Controller in GSC

## Slide 17: Positive Sequence GSC Control of GSC Power Q_GSC

## Slide 18: Positive Sequence GSC Control of DC Link Voltage VDC

## Slide 19: DFIG Grid Side Converter Negative Sequence Control
For negative sequence compensation via GSC, the current controllers of the GSC will measure the network currents, extract the negative sequence components and generate the required negative sequence currents from the GSC for compensation.
The reference values of the negative sequence currents come from the measurements of the currents to the grid.

## Slide 20: Negative Sequence Controller in GSC

## Slide 21: Negative Sequence Compensation via GSC

## Slide 22: Stator Currents

## Slide 23: Rotor Currents

## Slide 24: Rotor Voltages

## Slide 25: GSC Currents

## Slide 26: Grid Currents

## Slide 27: Summary
Due to unbalanced stator voltage conditions, negative-sequence components in stator currents induce a high frequency component (ωe+ωm) or (2−s)ωe in rotor currents and pulsations at 2ωe frequency in electromagnetic torques.
GSC compensate the negative sequence currents required in the network during any unbalanced operation. It also controls Power delivered to grid by GSC and DC Link Voltage.
RSC has the potential to eliminate negative sequence rotor currents, negative sequence stator currents or torque pulsation. It also controls Active and Reactive Power delivered by stator.

## Slide 28: References
L. Fan and Z. Miao, Modeling and Analysis of Doubly Fed Induction Generator Wind Energy Systems, Elsevier Ltd., 2015, 1-78.
R. Pena, J. Clare, G. Asher, Doubly fed induction generator using back-to-back pwm converters and its application to variable-speed wind-energy generation, IEEE Proc. Electr. Power Appl. 143(3), 1996, 231-241.
R. Pena, R. Cardenas, E. Escobar, Control system for unbalanced operation of stand-alone doubly fed induction generators, IEEE Trans. Energy Convers. 22(2), 2007, 544-545.